# MTIBS Tag Pattern Guide - Hoglund / Polish HMA Projects

This guide describes the MTIBS tag patterns found in Polish HMA projects implemented by a third party (Hoglund). The spreadsheet layout is the same GenSheet / List / detail-workbook model as other IBS vessels, but the tag naming style is different from the MT in-house pattern documented in mtibs-tag-pattern-guide.md.

Research sample: Polish HMA Projects GenSheet set for Remontowa B851 (files such as Gmr100.xls, RemontowaB851_4_MAIN.xls, RemontowaB851_4_COM.xls, RemontowaB851_4_PMS.xls). Source Excel files stay local and are not copied to GitHub.

| List source | MTIBS rows | Tags | Unique tags | Bool tags | Real tags |
| --- | --- | --- | --- | --- | --- |
| Gmr100.xls | 69 | 2167 | 2167 | 1751 | 416 |

## What MTIBS Sends

MTIBS is an MT proprietary telegram used to send IBS data to shore. The List tab in Gmr100.xls defines how many MTIBS telegrams are sent and which tags are included in each telegram.

A typical row looks like:

$MTIBS1,1,1,1,1,7.50,4.20,3.10,0.15,1,2.10,1.80,1,1,1,1,45.00,50.00,80.00,82.00,85.00,78.00,70.00,65.00,1,1,0,1,1,1,0*4A

The first column is usually the telegram name, the second is the telegram number, and the remaining cells are comma-separated tag definitions.

## List Token Format

| Token part | Meaning |
| --- | --- |
| T | Data point/tag entry. |
| B | Boolean value. Interpret as 0/1, commonly closed/open, off/on, normal/alarm, or false/true depending on the tag description. |
| R | Real value. Interpret as a numeric analog/derived value. Units must be resolved from the detail workbook or project context. |
| <tag> | The tag name to cross-reference in the Remontowa / MAIN / PMS sheets. |

Examples:

| Token | Interpretation |
| --- | --- |
| T,B=441_1_1_LS1 | Boolean low-level switch for DG1 LT tank water. |
| T,R=441_1_1_PS3 | Real starting-air pressure for DG1. |
| T,B=512_1_02_03_ZSH | Boolean opened status for FO valve 512.1-02.03. |
| T,R=512_1_A044_LT | Real level transmitter for FO EDG service tank A044. |

## Tag Name Families

Hoglund List tabs are dominated by short underscore-separated numeric tags. Compared with the MT in-house style (326_00051_ZS1), these tags use smaller middle segments and often encode P&ID valve or tank IDs directly.

| Family | Shape | Examples | Notes |
| --- | --- | --- | --- |
| Equipment / point tags | <system>_<group>_<unit>_<suffix> | 441_1_1_LS1, 511_2_2_ZS1, 512_1_1_PT1 | Most common for DG sensors, pumps, fans, and alarms. |
| Valve / line tags | <system>_<group>_<line>_<valve>[_suffix] | 512_1_02_03, 512_1_02_03_ZSH, 522_5_01_01_ZZL | Common on FO, dry-bulk, and methanol valves. Base object lives in BVAL. |
| Tank / A-code tags | <system>_<group>_A<nnn>[_suffix] | 512_1_A044, 512_1_A044_LT, 512_1_A026_LT | Tank objects in TK; level usually _LT rather than _LT1. |
| Base object tags | <system>_<group>_<unit> | 511_2_2, 513_1_1, 512_1_1 | Motor/object rows in MOT / BVAL / TK without a signal suffix. |
| Variant letter tags | <system>_<group>_<unit><letter> | 511_2_2E, 511_4_2E | Extra motor/object variant; resolve description in MOT. |
| Occasional MT-style tags | <system>_<5digit>_<suffix> | 404_10001_XI, 871_10099_ZZL | A small minority in this sample; treat like MT in-house tags when present. |
| Named tags | Word names | PRINTERCTRL | Rare; resolve in detail sheets by exact TagName. |

## Structured Numeric Tags

Typical Hoglund equipment/point tag:

441_1_1_LS1
|   | | |
|   | | suffix / signal role
|   | equipment or unit number
|   group / instance within the system
system or process family code

Typical valve tag:

512_1_02_03_ZSH
|   | |  |  |
|   | |  |  suffix / limit role
|   | |  valve number
|   | line or valve group
|   group / instance
system or process family code

Typical tank tag:

512_1_A044_LT
|   | |    |
|   | |    suffix / signal role
|   | tank A-code from project drawings / GenSheet
|   group / instance
system or process family code

### System / Process Code

The leading numeric code groups tags by vessel system. Always verify in the detail workbook because meanings are project-specific.

Observed examples from Remontowa B851:

| Code | Observed descriptions / context |
| --- | --- |
| 441 | Diesel generators (DG1?DG4) pressures, temperatures, levels, alarms, resets. |
| 442 | Heat-exchanger / DG boost and related cooling values. |
| 511 | Central cooling SW/FW pumps and related status/commands. |
| 512 | Fuel oil transfer pumps, FO valves, FO tanks. |
| 513 | Lub oil transfer / filter pumps. |
| 514 | Starting-air compressor alarms. |
| 521 | Bilge pumps. |
| 522 | Dry-bulk and methanol valves/pumps. |
| 531 | Fresh-water tank overflow / level alarms. |
| 551 | Fire pumps. |
| 562 | Engine-room fans. |
| 572 | Sewage treatment plant alarms. |
| 580 | Provision / HVAC compressor alarms. |
| 601 | Main HV transformer alarms (also a few MT-style 601_xxxxx tags). |
| 610 | Generator electrical values such as active power. |
| 611 | Azimuth thruster winding temperatures / machinery. |
| 613 | Fi-Fi system common alarm. |
| 614 | Azimuth thruster AQM oil level alarms. |
| 633 | Navigation lights common alarm. |
| 641 | GMDSS power-supply fail. |
| 663, 670, 672, 673 | UPS / AMS supply and insulation alarms. |
| 675 | Draught measurement. |
| 404 | Bridge/manual lever mode indicators (MT-style IDs in this sample). |

Treat this as a lookup hint, not a contract. The authoritative text is the matching Descr in the detail workbook.

### Group / Unit / Line Segments

Unlike MT in-house five-digit equipment numbers (00051, 10001), Hoglund middle segments are short and often mirror drawing numbers:

| Segment pattern | Typical meaning |
| --- | --- |
| second number (1, 2, 5, 6, ?) | Subsystem instance, side group, or package number. |
| third number (1, 2, 15, ?) | Equipment / unit number within that group. |
| third + fourth (02_03, 01_01, 22_04) | Valve line and valve number, often shown in descriptions as 512.1-02.03. |
| A026, A044, A049 | Tank A-codes used as the object ID in TK. |
| trailing letter on unit (2E) | Object variant; confirm in MOT. |

Examples:

| Base tag | Description evidence |
| --- | --- |
| 441_1_1 | DG1 points (DG1 STARTING AIR PRESSURE, DG1 LOW LT TANK WATER LEVEL). |
| 511_2_2 | Central cooling SW pump No.2. |
| 512_1_02_03 | FO valve No. 512.1-02.03. |
| 512_1_A044 | FO EDG service tank. |
| 522_5_01_01 | Methanol valve No. 522.5-01.01. |

### Suffix / Signal Role

Suffixes are largely the same ISA-style letters seen on MT projects, with a few Hoglund preferences.

| Suffix | Observed meaning / use | Typical type in MTIBS |
| --- | --- | --- |
| _PT, _PT1, _PT2 | Pressure transmitter / pressure analog. | T,R |
| _TT, _TT1?_TT8 | Temperature transmitter / temperature analog. | T,R |
| _LT | Tank level transmitter. Prefer _LT here; _LT1/_LT2 are less common than on MT in-house sheets. | T,R |
| _PS, _PS1? | Pressure switch or pressure alarm/status. Type follows List token (B or R). | T,B or T,R |
| _TS, _TS1? | Temperature switch / temperature status. | Usually T,B or T,R as listed |
| _LS, _LS1, _LS2 | Level switch / low-level alarm. | T,B |
| _RH | Running-hours / hours accumulator linked to running status. | T,R |
| _XA, _XA1, _XA2? | Alarm / fail / common-alarm indication. | T,B |
| _XC, _XC1, _XC2 | Command/control/reset outputs. Example: 441_1_1_XC1 = DG1 reset. | T,B |
| _XI, _XI1? | Indication / measured status or electrical indication. | T,B or T,R |
| _XY0 | Stop / close command. | T,B |
| _XY1 | Start / open command. | T,B |
| _ZS1 | Running / position status. | T,B |
| _HS1 | Local / auto or hand status. | T,B |
| _ZSH, _ZSL | Valve opened / closed status. | T,B |
| _ZZH, _ZZL | Valve open / close command (or related end positions depending on object wiring). On BVAL, Open/Close often reference ZZH/ZZL. | T,B |

The List token type (B or R) is authoritative for the value format sent in MTIBS.

## How To Resolve a Tag

Open Gmr100.xls and find the List tab.

Collect all T,B=<tag> and T,R=<tag> entries from MTIBS rows.

Search the Remontowa detail workbooks for exact TagName = <tag>. Start with RemontowaB851_4_MAIN.xls, then RemontowaB851_4_PMS.xls / RemontowaB851_4_COM.xls as needed.

If exact search fails, strip the final suffix and search the base object, for example search 511_2_2 for 511_2_2_ZS1, or 512_1_A044 for 512_1_A044_LT.

For valve tags, also search BVAL using the four-segment base (512_1_02_03) and read Open/Close/Opened/Closed reference columns.

Use the row's TaskName, Descr, and communication/reference columns to interpret the point.

Use the List token type for the transmitted value format: B boolean or R real.

## Useful Detail Sheets

Workbook names in this sample use the project prefix RemontowaB851_4_* instead of Hxxx_*, but the sheet families are the same.

| Sheet family | Workbook examples | What it usually contains | Useful columns |
| --- | --- | --- | --- |
| AIS, AIS02 | *_MAIN.xls, *_PMS.xls | Analog inputs / measured values. | TagName, Descr, ranges, alarm limits. |
| DIS, DIS02 | *_MAIN.xls, *_PMS.xls | Digital inputs / status / alarms. | TagName, Descr, NormPos, CommProvider/address/bit. |
| DOS | *_MAIN.xls | Digital outputs / commands. | TagName, Descr, pulse/command source. |
| AOS | *_MAIN.xls | Analog outputs. | TagName, Descr. |
| BVAL | *_MAIN.xls | Valve objects. | Base TagName, Descr, Open, Close, Opened, Closed, Local. |
| TK | *_MAIN.xls | Tank objects. | Base TagName, Descr, LT1/LT2 refs (often gv..._LT). |
| MOT | *_MAIN.xls | Motor/pump/fan objects. | Base TagName, Descr, Start, Stop, Running, Fail. |
| RunningHours | *_MAIN.xls | Hours accumulators. | TagName, Descr, input references. |
| MBTCP*, MBRead*, MBSlave | *_COM.xls | Communication mapping. | Register/coil mapping columns. |
| GEN, GenAdmin | *_PMS.xls | Generator / PMS objects. | Generator status and command tags. |

## Evidence Examples

These examples were cross-referenced from List tags into Remontowa B851 detail sheets.

| List tag | Detail evidence | Meaning inferred |
| --- | --- | --- |
| 441_1_1_LS1 | DIS: Descr=DG1 LOW LT TANK WATER LEVEL. | Boolean low-level switch for DG1 LT tank. |
| 441_1_1_PS3 | AIS: Descr=DG1 STARTING AIR PRESSURE. | Real DG1 starting-air pressure. |
| 441_1_2_TT7 | AIS: Descr=DG2 FRESH WATER TEMP OUTLET. | Real DG2 FW outlet temperature. |
| 441_1_1_XC1 | DOS: Descr=DG1 RESET. | Boolean reset command. |
| 511_2_2_ZS1 | DIS02: running status; MOT base 511_2_2 = Central cooling SW pump No.2. | Boolean pump running. |
| 511_2_2_HS1 | DIS02: CC SW PUMP2 LOCAL/AUTO. | Boolean local/auto status. |
| 511_2_2_XA | DIS: CENTRAL COOLING SW PUMP 2 FAILURE. | Boolean fail alarm. |
| 511_2_2_XY0 / _XY1 | DOS: stop / start commands. | Boolean stop and start outputs. |
| 511_2_2_RH | RunningHours: linked to pump running. | Real running-hours value. |
| 512_1_02_03_ZSH / _ZSL | DIS02: FO valve opened/closed; BVAL base 512_1_02_03. | Boolean valve position status. |
| 512_1_02_03 Open/Close refs | BVAL Open=gv512_1_02_03_ZZH, Close=gv512_1_02_03_ZZL, Opened/Closed use ZSH/ZSL. | ZZH/ZZL command side; ZSH/ZSL feedback side. |
| 512_1_A044_LT | AIS02: FO EDG service tank level; TK base 512_1_A044. | Real tank level. |
| 513_1_1_ZS1 | DIS02 + MOT clean LO transfer pump. | Boolean pump running. |
| 404_10001_XI | DIS02: BRIDGE IN MANUAL LEVER MODE. | Boolean bridge mode indication using MT-style ID. |

## Important Caveats

The Hoglund tag shape is consistent enough for discovery, but final meaning still requires the detail workbook Descr row.

Do not assume MT in-house five-digit equipment IDs. Most tags here use short group/unit/line segments or tank A-codes.

_XY0 is stop/close and _XY1 is start/open in this sample. Confirm before mapping dashboards.

Valve command vs feedback can look similar (ZZH/ZZL vs ZSH/ZSL). Prefer BVAL reference columns over guessing from the suffix alone.

A few MT-style tags coexist in the same List. Resolve them the same way: exact TagName search, then base-tag fallback.

Workbook names are project-prefixed (RemontowaB851_4_MAIN.xls), but sheet families (AIS, DIS, MOT, BVAL, TK) match the usual IBS GenSheet model.